# [Customer]

# Compliance Monitoring Program Template

Project Name, Customer Name

XXXMW Example Generating System

Site Address

8/3/2022 – Version 1.0

Contents

Document Control	1

Reference Documents	2

Introduction	2

Operating Philosophy	2

Compliance Monitoring Program	3

## Document Control

| Version | Date | Author | Notes |
| --- | --- | --- | --- |
| 01 | 25/11/2020 | Joe Bloggs | Revision 1 |

# Reference Documents

| Engineering Report Number | ER 1234 |
| --- | --- |
| Engineering Report Revision | Rev A |
| Commissioning Plan Revision | Rev B |

# Introduction

| Site Address |  |
| --- | --- |
| NMI |  |
| Total Solar PV Approved Capacity | 1000 kVA (AC), 1300 kVA (DC) |
| Total Battery Approved Capacity | 0 kVA (AC), 0 kVA (DC) |
| Total Synchronous Approved Capacity | 0 kVA (AC) |
| Connection Point Power Factor | Unity |
| Maximum Export | 1000 kW (AC) |
| Minimum Import | - |
| Nominal Voltage | 230 V |
| Connection Date | 10/11/2020 |
| Site Contact Name | Joe Bloggs |
| Site Contact Mobile Phone Number | 0412 34 56 78 |

# Operating Philosophy

- Customer to update this operating philosophy section capturing detailed descriptions such as:

Possible modes of operation and the most likely operating scenarios (e.g. combination of generating units online etc.)

Description of different plant operating mode (main supply, backup, island etc.) and associated details on the following:

  - Changeover/switching procedures (e.g. live / dead)

  - Interlocking arrangement

  - Setting changes required

  - Any other relevant site-specific constraints / operating conditions e.g. non-export

# Compliance Monitoring Program

| Performance Standard/Rules/Code Provision | Testing and Monitoring Methodology | Compliance Criteria | Testing Frequency | Resp Party | Notes | Documentation |
| --- | --- | --- | --- | --- | --- | --- |
| Protection Requirements |  |  |  |  |  |  |
| Generating System Protection Settings | Routine testing and / or calibration of protection systems including: - CB Opening times - Protection relay injection testing to trip - Sub-system testing by secondary injection testing - Visual confirmation of inverter settings | All applicable generator protection relays including but not limited to: ROCOF, Under/Over Frequency, Under/Over Voltages, to operate satisfactorily and to within tolerance of settings | Every 3 years and following any protection changes | Customer | Directly measurable, Check against approved setting sheet provided to SAPN Includes loss of mains relay for ROCOF, under/over Voltages and Frequency, protection relays for HV circuit breakers | Secondary Injection test results of the protection relay(s) Visual evidence/ confirmation of applied inverter settings |
| Protection Equipment including fault current limiters, NER/X | Performance monitored as part of in-service condition monitoring inspection and maintenance schedules | Meets performance requirements and completed against maintenance schedule | As per schedule requirements | Customer | External maintenance contract with authorized contractor. Critical spares to be stored on site. | Completed maintenance schedule |
| Power Quality Requirements |  |  |  |  |  |  |
| Voltage Fluctuation and Flicker | In-service power quality monitoring and analysis as per the relevant technical standards | Voltage disturbances not exceed allocation levels specified in the Engineering Report | Every 3 years and after plant change event | Customer | Access standard values allocated by service provider SAPN. Recorded at Connection Point. | 7-day voltage flicker (Pst, Plt) data with 10-min averages. |
| Harmonics | In-service power quality monitoring and analysis as per the relevant technical standards | Harmonic Distortion Limits not to exceed allocations levels specified in the Engineering Report | Every 3 years and after plant change event | Customer | Access standard values allocated by service provider SAPN. Recorded at Connection Point. | 7-day harmonics (individual up to 50th including THD) data with 10-min averages. |
| Voltage Unbalance | In-service power quality monitoring and analysis as per the relevant technical standards | The Voltage Unbalance values not exceed levels specified in the Engineering Report | Every 3 years and after plant change event | Customer | Access standard values allocated by service provider SAPN. Recorded at Connection Point. | 7-day voltage unbalance data with 10-min averages. |
| Steady State Voltage | In-service power quality monitoring | Measured voltage shall not exceed levels specified in the Engineering Report | Every 3 years and after plant change event | Customer and SAPN | Recorded at Connection Point. | 7-day voltage measurement with 3 sec intervals. |
| Reactive Power Capability | At rated power output, adjust the power factor at the connection point. Monitor using SCADA and issue setpoint via SAPN NOC. | Comply with power factor requirements at the connection point as per specifications in the Engineering Report | Every 3 years and after plant or reactive equipment change | Customer | Recorded at Connection Point. | Summary of results upon completion of set points test with SAPN NOC |
| Remote Monitoring and Control Requirements |  |  |  |  |  |  |
| Remote Monitoring and Set Points Control | Verify SCADA monitored values. Test all set points eg. power factor, GDL, NEL. Test permissive signalling. | SCADA controls function as intended, SCADA monitoring values within tolerances and updates without unintentional delays | Every 3 years and after plant or control system change. | Customer and SAPN NOC | Confirmation at each end by both parties | Summary of results upon completion of set points test with SAPN NOC |
| Communications Equipment | Confirmation of the availability of communication I/O. Force communications link drop out. | All necessary permissive signalling to be fail-safe in the event of loss of communications for 60 seconds. | Every 3 years and after plant or control system change. | Customer and SAPN NOC | Loss of communications should result in a ‘Permission to Connect Denied’ signal from SAPN | Summary of results upon completion of set points test with SAPN NOC |
| Ramp Rate | Performance monitored in-service on SCADA. Load and unload system to confirm ramp rate meets criteria. | Demonstrate ramp rate requirements as per Engineering Report. | Every 3 years and after plant change event | Customer and SAPN NOC |  | Summary of results upon completion of set points test with SAPN NOC |

For Synchronous Generating Systems, please include in addition:

| Performance Standard/Rules/Code Provision | Testing and Monitoring Methodology | Compliance Criteria | Testing Frequency | Resp Person | Notes | Documentation |
| --- | --- | --- | --- | --- | --- | --- |
| Fault Level Contribution | - Monitoring in-service performance during faults near the connection point. - Review and recalculation of fault levels - Routine testing of any relevant sub-systems - Obtain fault level contribution from network provider | Fault contribution as specified in the Engineering Report not to be exceeded at point of connection | Upon request by SAPN | Customer | Confirm with SAPN if an actual fault level value can be provided for connection point and compare to modelling data | Results of fault current recorders upon being requested by SAPN |
| Synchronizing Checks | Test Auto Sync Relay and Dead Bus check operate correctly | Performance confirmed by the generator prevented from synchronizing when internal network is de-energized or from forced fault event | Every 3 years and after plant change event. | Customer |  | Test results |

| Signoff |  |
| --- | --- |
| Compliance Monitoring Plan Approved Date: |  |
| Next Compliance Monitoring Scheduled Check Date: |  |